## Fact Sheet
EFFICIENT ELECTRIFICATION INTERACTIVE FACT SHEET
This Interactive Fact Sheet allows users to view the financial and carbon emissions impacts of electrifying building heating and cooling by replacing a rooftop unit (RTU) with an air-source heat pump (ASHP).
DID YOU KNOW…?
Replacing an aging rooftop unit (RTU) with an air-source heat pump reduces carbon emissions and may deliver a return on investment?
Adjust the parameters in bold below to quickly estimate the costs and benefits for your situation.
Static Parameters
Floor area (ft2) | 50000
Existing RTU efficiency: | 85%
New equipment COP* (cooling): | 5
New equipment seasonal efficiency (heating) | 230%
Adjustible Parameters |  | Parameters Explained
My RTU fuel is: | Natural Gas | New equipment type:
New equipment type: | ASHP hybrid system | ASHP | The air source heat pump is sized to meet 100% of the building heating load
I am located in: | Ottawa | ASHP Hybrid System | The air source heat pump is sized to meet 50% of the building heating load, so the building will rely on the heat pump and backup heating systems during the coldest days.
My building insulation condition: | Medium | Building insulation condition is based on the Insulation Condition parameter in the RETScreen Expert® Clean Energy Management Software. Better insulation condition corresponds to a lower heating load for the building.
Energy efficiency measures | No measures | Energy efficiency measures estimates the impacts of including a bundle of energy efficiency measures as part of the heat pump project. The project outcomes and financial metrics include the additional project costs (including installation costs) and energy performance benefits for the selected energy efficiency measure bundle.
PROJECT OUTCOMES
Annual operating cost savings | 3320
Carbon emissions impact | -87.1%
FINANCIAL METRICS
Savings to investment ratio: | 0.38
Internal rate of return: | -4.3%
Net present value: | -53691
Simple payback (years): | 26
$/ton carbon avoided: | 307
DID YOU KNOW…?
Investing in energy efficiency projects could reduce your heating energy consumption by more than 50%, dramatically reducing the cost of your new heat pump
Energy Efficiency Upgrade | Heating Energy Savings
Demand Control Ventilation | up to 40%
Heat recovery | up to 30%
Air Sealing | 10 - 20%
Results were simulated using the RETScreen Expert® Clean Energy Management Software, developed and maintained by Natural Resources Canada. More information about RETScreen is available at
https://www.nrcan.gc.ca/maps-tools-and-publications/tools/modelling-tools/retscreen/7465.

## Parameters
RTU Fuel | New Equipment Type
Propane | ASHP
Natural Gas | ASHP hybrid system
Location | Level of insulation
Ottawa | Good
Thunder Bay | Medium
Kingston | Poor
Toronto
EE Measures
No measures
Demand Control Ventilation
Demand Control Ventilation and Heat Recovery
Demand Control Ventilation, Air Sealing and Heat Recovery

## Graphs (hidden)
Location | Energy Efficiency | Somme de Net Present Value
Kingston | No measures | 345592
Kingston | Demand Control Ventilation, Air Sealing and Heat Recovery | 2394167
Kingston | Demand Control Ventilation and Heat Recovery | 1693732
Kingston | Demand Control Ventilation | 1035615
Ottawa | No measures | 346040
Ottawa | Demand Control Ventilation, Air Sealing and Heat Recovery | 2533286
Ottawa | Demand Control Ventilation and Heat Recovery | 1781612
Ottawa | Demand Control Ventilation | 1089068
Thunder Bay | No measures | 440404
Thunder Bay | Demand Control Ventilation, Air Sealing and Heat Recovery | 2868203
Thunder Bay | Demand Control Ventilation and Heat Recovery | 2034404
Thunder Bay | Demand Control Ventilation | 1259110
Total général |  | 17821233
Location | Energy Efficiency | Moyenne de Simple Payback (yr)
Kingston | No measures | 19.9417
Kingston | Demand Control Ventilation, Air Sealing and Heat Recovery | 4.2
Kingston | Demand Control Ventilation and Heat Recovery | 6.2167
Kingston | Demand Control Ventilation | 9.8167
Ottawa | No measures | 21.2833
Ottawa | Demand Control Ventilation, Air Sealing and Heat Recovery | 4.05
Ottawa | Demand Control Ventilation and Heat Recovery | 6.15
Ottawa | Demand Control Ventilation | 9.7
Thunder Bay | No measures | 23.3
Thunder Bay | Demand Control Ventilation, Air Sealing and Heat Recovery | 3.675
Thunder Bay | Demand Control Ventilation and Heat Recovery | 5.8
Thunder Bay | Demand Control Ventilation | 9.7083
Total général |  | 10.3201
Insulation | RTU Fuel | Location | Energy Efficiency | Somme de Simple Payback (yr)
Medium | Natural Gas | Kingston | Demand Control Ventilation, Air Sealing and Heat Recovery | 11.4
Medium | Natural Gas | Kingston | Demand Control Ventilation and Heat Recovery | 17.9
Medium | Natural Gas | Kingston | Demand Control Ventilation | 30.4
Medium | Natural Gas | Kingston | No measures | 69.7
Medium | Natural Gas | Ottawa | Demand Control Ventilation, Air Sealing and Heat Recovery | 11.4
Medium | Natural Gas | Ottawa | Demand Control Ventilation and Heat Recovery | 18.1
Medium | Natural Gas | Ottawa | Demand Control Ventilation | 30.8
Medium | Natural Gas | Ottawa | No measures | 72
Medium | Natural Gas | Thunder Bay | Demand Control Ventilation, Air Sealing and Heat Recovery | 10.3
Medium | Natural Gas | Thunder Bay | Demand Control Ventilation and Heat Recovery | 17
Medium | Natural Gas | Thunder Bay | Demand Control Ventilation | 30.6
Medium | Natural Gas | Thunder Bay | No measures | 82.6
Medium | Propane | Kingston | Demand Control Ventilation, Air Sealing and Heat Recovery | 5
Medium | Propane | Kingston | Demand Control Ventilation and Heat Recovery | 6.7
Medium | Propane | Kingston | Demand Control Ventilation | 8.7
Medium | Propane | Kingston | No measures | 11.5
Medium | Propane | Ottawa | Demand Control Ventilation, Air Sealing and Heat Recovery | 4.6
Medium | Propane | Ottawa | Demand Control Ventilation and Heat Recovery | 6.7
Medium | Propane | Ottawa | Demand Control Ventilation | 8.7
Medium | Propane | Ottawa | No measures | 11.5
Medium | Propane | Thunder Bay | Demand Control Ventilation, Air Sealing and Heat Recovery | 4.4
Medium | Propane | Thunder Bay | Demand Control Ventilation and Heat Recovery | 5.9
Medium | Propane | Thunder Bay | Demand Control Ventilation | 8
Medium | Propane | Thunder Bay | No measures | 10.6
Poorly | Natural Gas | Kingston | Demand Control Ventilation, Air Sealing and Heat Recovery | 10.5
Poorly | Natural Gas | Kingston | Demand Control Ventilation and Heat Recovery | 17.1
Poorly | Natural Gas | Kingston | Demand Control Ventilation | 29.8
Poorly | Natural Gas | Kingston | No measures | 69.6
Poorly | Natural Gas | Ottawa | Demand Control Ventilation, Air Sealing and Heat Recovery | 10.2
Poorly | Natural Gas | Ottawa | Demand Control Ventilation and Heat Recovery | 16.9
Poorly | Natural Gas | Ottawa | Demand Control Ventilation | 28
Poorly | Natural Gas | Ottawa | No measures | 77.3
Poorly | Natural Gas | Thunder Bay | Demand Control Ventilation, Air Sealing and Heat Recovery | 9.7
Poorly | Natural Gas | Thunder Bay | Demand Control Ventilation and Heat Recovery | 16.5
Poorly | Natural Gas | Thunder Bay | Demand Control Ventilation | 30.2
Poorly | Natural Gas | Thunder Bay | No measures | 82.4
Poorly | Propane | Kingston | Demand Control Ventilation, Air Sealing and Heat Recovery | 4.6
Poorly | Propane | Kingston | Demand Control Ventilation and Heat Recovery | 6.3
Poorly | Propane | Kingston | Demand Control Ventilation | 8.5
Poorly | Propane | Kingston | No measures | 11.5
Poorly | Propane | Ottawa | Demand Control Ventilation, Air Sealing and Heat Recovery | 4.4
Poorly | Propane | Ottawa | Demand Control Ventilation and Heat Recovery | 6.1
Poorly | Propane | Ottawa | Demand Control Ventilation | 8.4
Poorly | Propane | Ottawa | No measures | 11.3
Poorly | Propane | Thunder Bay | Demand Control Ventilation, Air Sealing and Heat Recovery | 4.2
Poorly | Propane | Thunder Bay | Demand Control Ventilation and Heat Recovery | 5.8
Poorly | Propane | Thunder Bay | Demand Control Ventilation | 7.9
Poorly | Propane | Thunder Bay | No measures | 10.8
Well | Natural Gas | Kingston | Demand Control Ventilation, Air Sealing and Heat Recovery | 13
Well | Natural Gas | Kingston | Demand Control Ventilation and Heat Recovery | 19.3
Well | Natural Gas | Kingston | Demand Control Ventilation | 31.1
Well | Natural Gas | Kingston | No measures | 65.2
Well | Natural Gas | Ottawa | Demand Control Ventilation, Air Sealing and Heat Recovery | 12.4
Well | Natural Gas | Ottawa | Demand Control Ventilation and Heat Recovery | 19.1
Well | Natural Gas | Ottawa | Demand Control Ventilation | 31.6
Well | Natural Gas | Ottawa | No measures | 71.8
Well | Natural Gas | Thunder Bay | Demand Control Ventilation, Air Sealing and Heat Recovery | 10.5
Well | Natural Gas | Thunder Bay | Demand Control Ventilation and Heat Recovery | 18.1
Well | Natural Gas | Thunder Bay | Demand Control Ventilation | 31.6
Well | Natural Gas | Thunder Bay | No measures | 82.4
Well | Propane | Kingston | Demand Control Ventilation, Air Sealing and Heat Recovery | 5.9
Well | Propane | Kingston | Demand Control Ventilation and Heat Recovery | 7.3
Well | Propane | Kingston | Demand Control Ventilation | 9.3
Well | Propane | Kingston | No measures | 11.8
Well | Propane | Ottawa | Demand Control Ventilation, Air Sealing and Heat Recovery | 5.6
Well | Propane | Ottawa | Demand Control Ventilation and Heat Recovery | 6.9
Well | Propane | Ottawa | Demand Control Ventilation | 8.9
Well | Propane | Ottawa | No measures | 11.5
Well | Propane | Thunder Bay | Demand Control Ventilation, Air Sealing and Heat Recovery | 5
Well | Propane | Thunder Bay | Demand Control Ventilation and Heat Recovery | 6.3
Well | Propane | Thunder Bay | Demand Control Ventilation | 8.2
Well | Propane | Thunder Bay | No measures | 10.8
Grand Total |  |  |  | 1486.1

## Result of simulation
[5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
Location | Insulation | New equipment type | RTU Fuel | Energy Efficiency | Helper | Heating design temperature (dgc C) | Cooling design temperature | Heating Load for Building (60W/m2) | Cooling Load for Building (W/m2) | Gross annual GHG emission (tCO2) | Gross annual GHG emission (%) | GHG reduction cost ($/tCO2) | Benefit-Cost Ratio | Simple Payback (yr) | Net Present Value | Internal Return on Investment | Initial difference in operating cost
Ottawa | Good | ASHP | Natural Gas | No measures | Ottawa¦Good¦ASHP¦Natural Gas¦No measures | -21.8 | 28.9 | 60 | 35 | -31.3 | -93% | 444 | 0.2 | 45.8 | -98430 | -9.4% | 2700
Ottawa | Medium | ASHP | Natural Gas | No measures | Ottawa¦Medium¦ASHP¦Natural Gas¦No measures | -21.8 | 28.9 | 70 | 40 | -36.5 | -93% | 444 | 0.2 | 46 | -114640 | -9.5% | 3120
Ottawa | Poor | ASHP | Natural Gas | No measures | Ottawa¦Poor ¦ASHP¦Natural Gas¦No measures | -21.8 | 28.9 | 84 | 45 | -43.8 | -93% | 474 | 0.18 | 51.1 | -152735 | -10.5% | 3636
Thunder Bay | Good | ASHP | Natural Gas | No measures | Thunder Bay¦Good¦ASHP¦Natural Gas¦No measures | -27 | 27 | 64 | 32.5 | -35.8 | -93.3% | 435 | 0.15 | 53.2 | -108952 | -12.6% | 2413
Thunder Bay | Medium | ASHP | Natural Gas | No measures | Thunder Bay¦Medium¦ASHP¦Natural Gas¦No measures | -27 | 27 | 77 | 38 | -43.1 | -93.3% | 434 | 0.15 | 53.4 | -130439 | -12.8% | 2878
Thunder Bay | Poor | ASHP | Natural Gas | No measures | Thunder Bay¦Poor ¦ASHP¦Natural Gas¦No measures | -27 | 27 | 86 | 43.5 | -48.1 | -93.3% | 435 | 0.15 | 53.2 | -146114 | -12.7% | 3239
Toronto | Good | ASHP | Natural Gas | No measures | Toronto¦Good¦ASHP¦Natural Gas¦No measures | -17.1 | 28.8 | 55 | 34 | 28.8 | 92.9% | 444 | 0.21 | 44.9 | -905733 | 9.1% | 2555
Toronto | Medium | ASHP | Natural Gas | No measures | Toronto¦Medium¦ASHP¦Natural Gas¦No measures | -17.1 | 28.8 | 65 | 40 | -33.5 | -92.8% | 438 | 0.24 | 41.1 | -102911 | -7.9% | 3296
Toronto | Poor | ASHP | Natural Gas | No measures | Toronto¦Poor ¦ASHP¦Natural Gas¦No measures | -17.1 | 28.8 | 75 | 45 | -39.3 | -93% | 443 | 0.21 | 45.2 | -123193 | -9.2% | 3434
Kingston | Good | ASHP | Natural Gas | No measures | Kingston¦Good¦ASHP¦Natural Gas¦No measures | -19 | 26.1 | 58 | 32 | -29.8 | -92.6% | 447 | 0.25 | 40 | -94427 | -7.3% | 3159
Kingston | Medium | ASHP | Natural Gas | No measures | Kingston¦Medium¦ASHP¦Natural Gas¦No measures | -19 | 26.1 | 69 | 37 | -35.3 | -92.9% | 442 | 0.21 | 44.4 | -109953 | -9% | 3150
Kingston | Poor | ASHP | Natural Gas | No measures | Kingston¦Poor ¦ASHP¦Natural Gas¦No measures | -19 | 26.1 | 80 | 43 | -40.9 | 92.9% | 442 | 0.21 | 44.3 | -127499 | -9% | 3656
Ottawa | Good | ASHP | Propane | No measures | Ottawa¦Good¦ASHP¦Propane ¦No measures | -21.8 | 28.9 | 60 | 35 | -38.8 | -94.3% | -46.77 | 1.8 | 7.2 | 96374 | 14% | 17139
Ottawa | Medium | ASHP | Propane | No measures | Ottawa¦Medium¦ASHP¦Propane ¦No measures | -21.8 | 28.9 | 70 | 40 | -45.2 | -94.3% | -47.18 | 1.8 | 7.2 | 112632 | 14.1% | 19966
Ottawa | Poor | ASHP | Propane | No measures | Ottawa¦Poor ¦ASHP¦Propane ¦No measures | -21.8 | 28.9 | 84 | 45 | -54.2 | -94.3% | -48.4 | 1.8 | 7.1 | 135860 | 14.2% | 23851
Thunder Bay | Good | ASHP | Propane | No measures | Thunder Bay¦Good¦ASHP¦Propane ¦No measures | -27 | 27 | 64 | 32.5 | -44.3 | -94.5% | -55.78 | 1.9 | 6.8 | 114838 | 15.1% | 18989
Thunder Bay | Medium | ASHP | Propane | No measures | Thunder Bay¦Medium¦ASHP¦Propane ¦No measures | -27 | 27 | 77 | 38 | -53.3 | -94.5% | -56.54 | 1.9 | 6.7 | 138611 | 15.1% | 22820
Thunder Bay | Poor | ASHP | Propane | No measures | Thunder Bay¦Poor ¦ASHP¦Propane ¦No measures | -27 | 27 | 86 | 43.5 | -59.6 | -94.5% | -55.89 | 1.9 | 6.8 | 154383 | 15.1% | 25512
Toronto | Good | ASHP | Propane | No measures | Toronto¦Good¦ASHP¦Propane ¦No measures | -17.1 | 28.8 | 55 | 34 | -35.7 | -94.2% | -46.68 | 1.8 | 7.2 | 88686 | 13.9% | 15842
Toronto | Medium | ASHP | Propane | No measures | Toronto¦Medium¦ASHP¦Propane ¦No measures | -17.1 | 28.8 | 65 | 40 | -42.2 | -94.2% | -46.78 | 1.8 | 7.2 | 104852 | 14% | 18715
Toronto | Poor | ASHP | Propane | No measures | Toronto¦Poor ¦ASHP¦Propane ¦No measures | -17.1 | 28.8 | 75 | 45 | -48.6 | -94.2% | -47.3 | 1.8 | 7.2 | 121251 | 14% | 21553
Kingston | Good | ASHP | Propane | No measures | Kingston¦Good¦ASHP¦Propane ¦No measures | -19 | 26.1 | 58 | 32 | -36.8 | -93.3% | -42.85 | 1.7 | 7.5 | 89843 | 13.4% | 16818
Kingston | Medium | ASHP | Propane | No measures | Kingston¦Medium¦ASHP¦Propane ¦No measures | -19 | 26.1 | 69 | 37 | -43.6 | -94.2% | -48.27 | 1.8 | 7.2 | 109264 | 14% | 19399
Kingston | Poor | ASHP | Propane | No measures | Kingston¦Poor ¦ASHP¦Propane ¦No measures | -19 | 26.1 | 80 | 43 | -50.6 | -94.2% | -48.24 | 1.8 | 7.2 | 126666 | 14% | 22495
Ottawa | Good | ASHP hybrid system | Natural Gas | No measures | Ottawa¦Good¦ASHP hybrid system¦Natural Gas¦No measures | -21.8 | 28.9 | 60 | 35 | -29.4 | -87.1% | 308 | 0.38 | 26 | -46391 | -4.3% | 2870
Ottawa | Medium | ASHP hybrid system | Natural Gas | No measures | Ottawa¦Medium¦ASHP hybrid system¦Natural Gas¦No measures | -21.8 | 28.9 | 70 | 40 | -34.2 | -87.1% | 307 | 0.38 | 26 | -53691 | -4.3% | 3320
Ottawa | Poor | ASHP hybrid system | Natural Gas | No measures | Ottawa¦Poor ¦ASHP hybrid system¦Natural Gas¦No measures | -21.8 | 28.9 | 84 | 45 | -41.1 | -87.2% | 306 | 0.37 | 26.2 | -63931 | -4.5% | 3875
Thunder Bay | Good | ASHP hybrid system | Natural Gas | No measures | Thunder Bay¦Good¦ASHP hybrid system¦Natural Gas¦No measures | -27 | 27 | 64 | 32.5 | -33.6 | -87.6% | 307 | 0.3 | 29.2 | -52951 | -6.7% | 2603
Thunder Bay | Medium | ASHP hybrid system | Natural Gas | No measures | Thunder Bay¦Medium¦ASHP hybrid system¦Natural Gas¦No measures | -27 | 27 | 77 | 38 | -40.4 | -87.6% | 307 | 0.3 | 29.2 | -63361 | -6.8% | 3104
Thunder Bay | Poor | ASHP hybrid system | Natural Gas | No measures | Thunder Bay¦Poor ¦ASHP hybrid system¦Natural Gas¦No measures | -27 | 27 | 86 | 43.5 | -45.2 | -87.6% | 307 | 0.3 | 29.2 | -71083 | -6.7% | 3493
Toronto | Good | ASHP hybrid system | Natural Gas | No measures | Toronto¦Good¦ASHP hybrid system¦Natural Gas¦No measures | -17.1 | 28.8 | 55 | 34 | -27 | -87.1% | 308 | 0.39 | 25.7 | -42720 | -4% | 2710
Toronto | Medium | ASHP hybrid system | Natural Gas | No measures | Toronto¦Medium¦ASHP hybrid system¦Natural Gas¦No measures | -17.1 | 28.8 | 65 | 40 | -31.9 | -87.1% | 308 | 0.39 | 25.7 | -50445 | -4.1% | 3196
Toronto | Poor | ASHP hybrid system | Natural Gas | No measures | Toronto¦Poor ¦ASHP hybrid system¦Natural Gas¦No measures | -17.1 | 28.8 | 75 | 45 | -36.8 | -87.1% | 307 | 0.38 | 25.8 | -57938 | -4.1% | 3646
Kingston | Good | ASHP hybrid system | Natural Gas | No measures | Kingston¦Good¦ASHP hybrid system¦Natural Gas¦No measures | -19 | 26.1 | 58 | 32 | -28.3 | -88.5% | 302 | 0.39 | 25.2 | -42906 | -3.9% | 2804
Kingston | Medium | ASHP hybrid system | Natural Gas | No measures | Kingston¦Medium¦ASHP hybrid system¦Natural Gas¦No measures | -19 | 26.1 | 69 | 37 | -33.6 | -88.6% | 302 | 0.39 | 25.3 | -50871 | -4% | 3292
Kingston | Poor | ASHP hybrid system | Natural Gas | No measures | Kingston¦Poor ¦ASHP hybrid system¦Natural Gas¦No measures | -19 | 26.1 | 80 | 43 | -39 | -88.6% | 302 | 0.39 | 25.3 | -58997 | -4% | 3821
Ottawa | Good | ASHP hybrid system | Propane | No measures | Ottawa¦Good¦ASHP hybrid system¦Propane ¦No measures | -21.8 | 28.9 | 60 | 35 | -36.8 | -89.4% | -182 | 3 | 4.3 | 148616 | 24.5% | 17311
Ottawa | Medium | ASHP hybrid system | Propane | No measures | Ottawa¦Medium¦ASHP hybrid system¦Propane ¦No measures | -21.8 | 28.9 | 70 | 40 | -42.9 | -89.5% | -182 | 3 | 4.3 | 173378 | 24.6% | 20164
Ottawa | Poor | ASHP hybrid system | Propane | No measures | Ottawa¦Poor ¦ASHP hybrid system¦Propane ¦No measures | -21.8 | 28.9 | 84 | 45 | -51.4 | -89.4% | -184 | 3.1 | 4.2 | 208998 | 25% | 24092
Thunder Bay | Good | ASHP hybrid system | Propane | No measures | Thunder Bay¦Good¦ASHP hybrid system¦Propane ¦No measures | -27 | 27 | 64 | 32.5 | -42.2 | -89.9% | -182 | 3.2 | 4 | 170269 | 26.5% | 19174
Thunder Bay | Medium | ASHP hybrid system | Propane | No measures | Thunder Bay¦Medium¦ASHP hybrid system¦Propane ¦No measures | -27 | 27 | 77 | 38 | -50.7 | -89.8% | -184 | 3.3 | 3.9 | 205789 | 26.8% | 23048
Thunder Bay | Poor | ASHP hybrid system | Propane | No measures | Thunder Bay¦Poor ¦ASHP hybrid system¦Propane ¦No measures | -27 | 27 | 86 | 43.5 | -56.6 | -89.8% | -183 | 3.3 | 4 | 229414 | 26.6% | 25767
Toronto | Good | ASHP hybrid system | Propane | No measures | Toronto¦Good¦ASHP hybrid system¦Propane ¦No measures | -17.1 | 28.8 | 55 | 34 | -33.9 | -89.4% | -181 | 4.4 | 3 | 136539 | 24.2% | 15997
Toronto | Medium | ASHP hybrid system | Propane | No measures | Toronto¦Medium¦ASHP hybrid system¦Propane ¦No measures | -17.1 | 28.8 | 65 | 40 | -40 | -89.4% | -182 | 4.3 | 3 | 161406 | 24.2% | 18899
Toronto | Poor | ASHP hybrid system | Propane | No measures | Toronto¦Poor ¦ASHP hybrid system¦Propane ¦No measures | -17.1 | 28.8 | 75 | 45 | -46.2 | -89.5% | -182 | 4.3 | 3 | 186505 | 24.4% | 21765
Kingston | Good | ASHP hybrid system | Propane | No measures | Kingston¦Good¦ASHP hybrid system¦Propane ¦No measures | -19 | 26.1 | 58 | 32 | -35.3 | -90.7% | -178 | 3 | 4.3 | 141161 | 24.5% | 16461
Kingston | Medium | ASHP hybrid system | Propane | No measures | Kingston¦Medium¦ASHP hybrid system¦Propane ¦No measures | -19 | 26.1 | 69 | 37 | -48.7 | -90.7% | -179 | 3 | 4.3 | 194965 | 24.7% | 16998
Kingston | Poor | ASHP hybrid system | Propane | No measures | Kingston¦Poor ¦ASHP hybrid system¦Propane ¦No measures | -19 | 26.1 | 80 | 43 | -42 | -90.6% | -180 | 3 | 4.3 | 168346 | 24.7% | 19541
Ottawa | Good | ASHP | Natural Gas | Demand Control Ventilation | Ottawa¦Good¦ASHP¦Natural Gas¦Demand Control Ventilation | -21.8 | 28.9 | 60 | 35 | -32 | -94.9% | 284 | 0.61 | 18.9 | -41821 | 0.63% | 5681
Ottawa | Medium | ASHP | Natural Gas | Demand Control Ventilation | Ottawa¦Medium¦ASHP¦Natural Gas¦Demand Control Ventilation | -21.8 | 28.9 | 70 | 40 | -37.3 | -95% | 278 | 0.62 | 18.5 | -46079 | 0.82% | 6596
Ottawa | Poor | ASHP | Natural Gas | Demand Control Ventilation | Ottawa¦Poor ¦ASHP¦Natural Gas¦Demand Control Ventilation | -21.8 | 28.9 | 84 | 45 | -44.7 | -95% | 271 | 0.63 | 18.2 | -51838 | 0.99% | 7800
Thunder Bay | Good | ASHP | Natural Gas | Demand Control Ventilation | Thunder Bay¦Good¦ASHP¦Natural Gas¦Demand Control Ventilation | -27 | 27 | 64 | 32.5 | -36.6 | -95.3% | 277 | 0.59 | 19.1 | -44916 | 0.29% | 5789
Thunder Bay | Medium | ASHP | Natural Gas | Demand Control Ventilation | Thunder Bay¦Medium¦ASHP¦Natural Gas¦Demand Control Ventilation | -27 | 27 | 77 | 38 | -44 | -95.3% | 270 | 0.61 | 18.6 | -50458 | 0.54% | 6938
Thunder Bay | Poor | ASHP | Natural Gas | Demand Control Ventilation | Thunder Bay¦Poor ¦ASHP¦Natural Gas¦Demand Control Ventilation | -27 | 27 | 86 | 43.5 | -49.1 | -95.3% | 267 | 0.62 | 18.4 | -54830 | 0.66% | 7775
Toronto | Good | ASHP | Natural Gas | Demand Control Ventilation | Toronto¦Good¦ASHP¦Natural Gas¦Demand Control Ventilation | -17.1 | 28.8 | 55 | 34 | -29.5 | -94.9% | 288 | 0.61 | 19.1 | -39760 | 0.57% | 5302
Toronto | Medium | ASHP | Natural Gas | Demand Control Ventilation | Toronto¦Medium¦ASHP¦Natural Gas¦Demand Control Ventilation | -17.1 | 28.8 | 65 | 40 | -34.8 | -94.9% | 280 | 0.62 | 18.6 | -44008 | 0.81% | 6269
Toronto | Poor | ASHP | Natural Gas | Demand Control Ventilation | Toronto¦Poor ¦ASHP¦Natural Gas¦Demand Control Ventilation | -17.1 | 28.8 | 75 | 45 | -40.1 | -94.9% | -275 | 0.63 | 18.3 | -48137 | 0.98% | 7178
Kingston | Good | ASHP | Natural Gas | Demand Control Ventilation | Kingston¦Good¦ASHP¦Natural Gas¦Demand Control Ventilation | -19 | 26.1 | 58 | 32 | -30.4 | -94.6% | 286 | 0.64 | 18.5 | -40316 | 1.1% | 6020
Kingston | Medium | ASHP | Natural Gas | Demand Control Ventilation | Kingston¦Medium¦ASHP¦Natural Gas¦Demand Control Ventilation | -19 | 26.1 | 69 | 37 | -36 | -94.9% | 275 | 0.63 | 18.3 | -43516 | 1% | 6512
Kingston | Poor | ASHP | Natural Gas | Demand Control Ventilation | Kingston¦Poor ¦ASHP¦Natural Gas¦Demand Control Ventilation | -19 | 26.1 | 80 | 43 | -41.8 | -94.9% | 270 | 0.65 | 18 | -47954 | 1.2% | 7554
Ottawa | Good | ASHP | Propane | Demand Control Ventilation | Ottawa¦Good¦ASHP¦Propane ¦Demand Control Ventilation | -21.8 | 28.9 | 60 | 35 | -39.4 | -95.9% | -168 | 2.4 | 5.3 | 152935 | 19.6% | 20120
Ottawa | Medium | ASHP | Propane | Demand Control Ventilation | Ottawa¦Medium¦ASHP¦Propane ¦Demand Control Ventilation | -21.8 | 28.9 | 70 | 40 | -46 | -95.9% | -174 | 2.5 | 5.2 | 181275 | 20.2% | 23442
Ottawa | Poor | ASHP | Propane | Demand Control Ventilation | Ottawa¦Poor ¦ASHP¦Propane ¦Demand Control Ventilation | -21.8 | 28.9 | 84 | 45 | -55.2 | -95.9% | -180 | 2.6 | 5.1 | 221134 | 20.8% | 28015
Thunder Bay | Good | ASHP | Propane | Demand Control Ventilation | Thunder Bay¦Good¦ASHP¦Propane ¦Demand Control Ventilation | -27 | 27 | 64 | 32.5 | -45.1 | -96.1% | -175 | 2.6 | 4.9 | 178628 | 21.3% | 22365
Thunder Bay | Medium | ASHP | Propane | Demand Control Ventilation | Thunder Bay¦Medium¦ASHP¦Propane ¦Demand Control Ventilation | -27 | 27 | 77 | 38 | -54.2 | -96.1% | -181 | 2.7 | 4.8 | 218474 | 22% | 26880
Thunder Bay | Poor | ASHP | Propane | Demand Control Ventilation | Thunder Bay¦Poor ¦ASHP¦Propane ¦Demand Control Ventilation | -27 | 27 | 86 | 43.5 | -60.6 | -96.1% | -183 | 2.7 | 4.8 | 245634 | 22.2% | 30048
Toronto | Good | ASHP | Propane | Demand Control Ventilation | Toronto¦Good¦ASHP¦Propane ¦Demand Control Ventilation | -17.1 | 28.8 | 55 | 34 | -36.3 | -95.8% | -165 | 2.4 | 5.4 | 139463 | 19.3% | 18589
Toronto | Medium | ASHP | Propane | Demand Control Ventilation | Toronto¦Medium¦ASHP¦Propane ¦Demand Control Ventilation | -17.1 | 28.8 | 65 | 40 | -42.9 | -95.8% | -171 | 2.4 | 5.3 | 167822 | 19.8% | 21962
Toronto | Poor | ASHP | Propane | Demand Control Ventilation | Toronto¦Poor ¦ASHP¦Propane ¦Demand Control Ventilation | -17.1 | 28.8 | 75 | 45 | -52.9 | -96.1% | -176 | 2.6 | 5 | 209867 | 21.2% | 26381
Kingston | Good | ASHP | Propane | Demand Control Ventilation | Kingston¦Good¦ASHP¦Propane ¦Demand Control Ventilation | -19 | 26.1 | 58 | 32 | -37.4 | -95.6% | -166 | 2.3 | 5.6 | 144213 | 18.6% | 19678
Kingston | Medium | ASHP | Propane | Demand Control Ventilation | Kingston¦Medium¦ASHP¦Propane ¦Demand Control Ventilation | -19 | 26.1 | 69 | 37 | -44.4 | -95.8% | -175 | 2.5 | 5.2 | 175701 | 20.1% | 22760
Kingston | Poor | ASHP | Propane | Demand Control Ventilation | Kingston¦Poor ¦ASHP¦Propane ¦Demand Control Ventilation | -19 | 26.1 | 80 | 43 | -51.5 | -95.8% | -179 | 2.5 | 5.1 | 206092 | 20.5% | 26393
Ottawa | Good | ASHP hybrid system | Natural Gas | Demand Control Ventilation | Ottawa¦Good¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation | -21.8 | 28.9 | 60 | 35 | -30.6 | -90.9% | 186 | 0.92 | 12.7 | -5710 | 5% | 5799
Ottawa | Medium | ASHP hybrid system | Natural Gas | Demand Control Ventilation | Ottawa¦Medium¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation | -21.8 | 28.9 | 70 | 40 | -35.7 | -90.9% | 180 | 0.95 | 12.3 | -3988 | 5.4% | 6733
Ottawa | Poor | ASHP hybrid system | Natural Gas | Demand Control Ventilation | Ottawa¦Poor ¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation | -21.8 | 28.9 | 84 | 45 | -42.8 | -90.9% | 140 | 1.2 | 9.8 | -988 | 5.9% | 7966
Thunder Bay | Good | ASHP hybrid system | Natural Gas | Demand Control Ventilation | Thunder Bay¦Good¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation | -27 | 27 | 64 | 32.5 | -35 | -91.3% | 186 | 0.92 | 12.5 | -6254 | 4.9% | 5920
Thunder Bay | Medium | ASHP hybrid system | Natural Gas | Demand Control Ventilation | Thunder Bay¦Medium¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation | -27 | 27 | 77 | 38 | -42.1 | -91.3% | 178 | 0.95 | 12 | -3960 | 5.4% | 7095
Thunder Bay | Poor | ASHP hybrid system | Natural Gas | Demand Control Ventilation | Thunder Bay¦Poor ¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation | -27 | 27 | 86 | 43.5 | -47.1 | -91.3% | 175 | 0.97 | 11.8 | -2968 | 5.6% | 7950
Toronto | Good | ASHP hybrid system | Natural Gas | Demand Control Ventilation | Toronto¦Good¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation | -17.1 | 28.8 | 55 | 34 | -28.2 | -90.9% | 190 | 0.91 | 12.9 | -6583 | 4.8% | 5409
Toronto | Medium | ASHP hybrid system | Natural Gas | Demand Control Ventilation | Toronto¦Medium¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation | -17.1 | 28.8 | 65 | 40 | -33.3 | -90.9% | 183 | 0.94 | 12.5 | -4882 | 5.2% | 6386
Toronto | Poor | ASHP hybrid system | Natural Gas | Demand Control Ventilation | Toronto¦Poor ¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation | -17.1 | 28.8 | 75 | 45 | -38.4 | -90.9% | 177 | 0.97 | 12.1 | -2980 | 5.6% | 7324
Kingston | Good | ASHP hybrid system | Natural Gas | Demand Control Ventilation | Kingston¦Good¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation | -19 | 26.1 | 58 | 32 | -29.3 | -91.9% | 185 | 0.93 | 12.6 | -4885 | 5.1% | 5595
Kingston | Medium | ASHP hybrid system | Natural Gas | Demand Control Ventilation | Kingston¦Medium¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation | -19 | 26.1 | 69 | 37 | -34.9 | -91.9% | 177 | 0.97 | 12.1 | -2680 | 5.6% | 6609
Kingston | Poor | ASHP hybrid system | Natural Gas | Demand Control Ventilation | Kingston¦Poor ¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation | -19 | 26.1 | 80 | 43 | -40.4 | -91.9% | 171 | 0.99 | 11.8 | -563 | 5.9% | 7668
Ottawa | Good | ASHP hybrid system | Propane | Demand Control Ventilation | Ottawa¦Good¦ASHP hybrid system¦Propane ¦Demand Control Ventilation | -21.8 | 28.9 | 60 | 35 | -38 | -92.5% | -263 | 3.6 | 3.6 | 189054 | 29.1% | 20238
Ottawa | Medium | ASHP hybrid system | Propane | Demand Control Ventilation | Ottawa¦Medium¦ASHP hybrid system¦Propane ¦Demand Control Ventilation | -21.8 | 28.9 | 70 | 40 | -44.4 | -92.5% | -269 | 3.7 | 3.5 | 223385 | 30.1% | 23580
Ottawa | Poor | ASHP hybrid system | Propane | Demand Control Ventilation | Ottawa¦Poor ¦ASHP hybrid system¦Propane ¦Demand Control Ventilation | -21.8 | 28.9 | 84 | 45 | -53.2 | -92.6% | -275 | 3.9 | 3.3 | 271709 | 31.7% | 28180
Toronto | Good | ASHP hybrid system | Propane | Demand Control Ventilation | Toronto¦Good¦ASHP hybrid system¦Propane ¦Demand Control Ventilation | -17.1 | 28.8 | 55 | 34 | -35 | -92.5% | -259 | 3.5 | 3.7 | 172639 | 28.2% | 18696
Toronto | Medium | ASHP hybrid system | Propane | Demand Control Ventilation | Toronto¦Medium¦ASHP hybrid system¦Propane ¦Demand Control Ventilation | -17.1 | 28.8 | 65 | 40 | -41.5 | -92.5% | -264 | 3.5 | 3.7 | 206229 | 28.3% | 22282
Toronto | Poor | ASHP hybrid system | Propane | Demand Control Ventilation | Toronto¦Poor ¦ASHP hybrid system¦Propane ¦Demand Control Ventilation | -17.1 | 28.8 | 75 | 45 | -47.8 | -92.5% | -271 | 3.7 | 3.5 | 241463 | 30.3% | 25443
Thunder Bay | Good | ASHP hybrid system | Propane | Demand Control Ventilation | Thunder Bay¦Good¦ASHP hybrid system¦Propane ¦Demand Control Ventilation | -27 | 27 | 64 | 32.5 | -43.6 | -92.9% | -265 | 3.9 | 3.3 | 217255 | 32% | 22495
Thunder Bay | Medium | ASHP hybrid system | Propane | Demand Control Ventilation | Thunder Bay¦Medium¦ASHP hybrid system¦Propane ¦Demand Control Ventilation | -27 | 27 | 77 | 38 | -52.4 | -92.9% | -271 | 4.1 | 3.2 | 264916 | 33.4% | 27037
Thunder Bay | Poor | ASHP hybrid system | Propane | Demand Control Ventilation | Thunder Bay¦Poor ¦ASHP hybrid system¦Propane ¦Demand Control Ventilation | -27 | 27 | 86 | 43.5 | -58.5 | -92.9% | -273 | 4.2 | 3.1 | 297589 | 33.8% | 30224
Kingston | Good | ASHP hybrid system | Propane | Demand Control Ventilation | Kingston¦Good¦ASHP hybrid system¦Propane ¦Demand Control Ventilation | -19 | 26.1 | 58 | 32 | -57.8 | -93.7% | -260 | 3.5 | 3.7 | 179384 | 28.9% | 19254
Kingston | Medium | ASHP hybrid system | Propane | Demand Control Ventilation | Kingston¦Medium¦ASHP hybrid system¦Propane ¦Demand Control Ventilation | -19 | 26.1 | 69 | 37 | -43.2 | -93.4% | -267 | 3.7 | 3.5 | 216537 | 30.2% | 22858
Kingston | Poor | ASHP hybrid system | Propane | Demand Control Ventilation | Kingston¦Poor ¦ASHP hybrid system¦Propane ¦Demand Control Ventilation | -19 | 26.1 | 80 | 43 | -50.1 | -93.3% | -271 | 3.8 | 3.4 | 253602 | 31% | 26507
Ottawa | Good | ASHP | Natural Gas | Demand Control Ventilation and Heat Recovery | Ottawa¦Good¦ASHP¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -21.8 | 28.9 | 60 | 35 | -32.6 | -96.7% | 137 | 1.1 | 10.8 | 12181 | 7.6% | 8371
Ottawa | Medium | ASHP | Natural Gas | Demand Control Ventilation and Heat Recovery | Ottawa¦Medium¦ASHP¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -21.8 | 28.9 | 70 | 40 | -38 | -96.7% | 127 | 1.2 | 10.3 | 18909 | 8.2% | 9732
Ottawa | Poor | ASHP | Natural Gas | Demand Control Ventilation and Heat Recovery | Ottawa¦Poor ¦ASHP¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -21.8 | 28.9 | 84 | 45 | -45.6 | -96.8% | 116 | 1.3 | 9.7 | 28385 | 8.9% | 11557
Thunder Bay | Good | ASHP | Natural Gas | Demand Control Ventilation and Heat Recovery | Thunder Bay¦Good¦ASHP¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -27 | 27 | 64 | 32.5 | -37.2 | -97% | 133 | 1.2 | 10.3 | 15764 | 8% | 8836
Thunder Bay | Medium | ASHP | Natural Gas | Demand Control Ventilation and Heat Recovery | Thunder Bay¦Medium¦ASHP¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -27 | 27 | 77 | 38 | -44.9 | -97% | 122 | 1.2 | 9.8 | 24768 | 8.7% | 10602
Thunder Bay | Poor | ASHP | Natural Gas | Demand Control Ventilation and Heat Recovery | Thunder Bay¦Poor ¦ASHP¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -27 | 27 | 86 | 43.5 | -50 | -97% | 117 | 1.3 | 9.5 | 30520 | 9.1% | 11869
Toronto | Good | ASHP | Natural Gas | Demand Control Ventilation and Heat Recovery | Toronto¦Good¦ASHP¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -17.1 | 28.8 | 55 | 34 | -30 | -96.7% | 143 | 1.1 | 11.1 | 9181 | 7.3% | 7782
Toronto | Medium | ASHP | Natural Gas | Demand Control Ventilation and Heat Recovery | Toronto¦Medium¦ASHP¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -17.1 | 28.8 | 65 | 40 | -35.5 | -96.7% | 131 | 1.2 | 10.5 | 15879 | 7.9% | 9189
Toronto | Poor | ASHP | Natural Gas | Demand Control Ventilation and Heat Recovery | Toronto¦Poor ¦ASHP¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -17.1 | 28.8 | 75 | 45 | -40.9 | -96.7% | 122 | 1.2 | 10.1 | 22507 | 8.4% | 10556
Kingston | Good | ASHP | Natural Gas | Demand Control Ventilation and Heat Recovery | Kingston¦Good¦ASHP¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -19 | 26.1 | 58 | 32 | -31 | -96.4% | 137 | 1.1 | 11 | 11725 | 7.4% | 8600
Kingston | Medium | ASHP | Natural Gas | Demand Control Ventilation and Heat Recovery | Kingston¦Medium¦ASHP¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -19 | 26.1 | 69 | 37 | -36.7 | -96.7% | 124 | 1.2 | 10.2 | 19378 | 8.3% | 9545
Kingston | Poor | ASHP | Natural Gas | Demand Control Ventilation and Heat Recovery | Kingston¦Poor ¦ASHP¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -19 | 26.1 | 80 | 43 | -42.5 | -96.7% | 115 | 1.2 | 9.8 | 26852 | 8.8% | 11072
Ottawa | Good | ASHP | Propane | Demand Control Ventilation and Heat Recovery | Ottawa¦Good¦ASHP¦Propane ¦Demand Control Ventilation and Heat Recovery | -21.8 | 28.9 | 60 | 35 | -40 | -97.3% | -281 | 3.3 | 3.9 | 207068 | 26.8% | 22810
Ottawa | Medium | ASHP | Propane | Demand Control Ventilation and Heat Recovery | Ottawa¦Medium¦ASHP¦Propane ¦Demand Control Ventilation and Heat Recovery | -21.8 | 28.9 | 70 | 40 | -46.7 | -97.3% | -290 | 3.5 | 3.8 | 246181 | 28.2% | 26578
Ottawa | Poor | ASHP | Propane | Demand Control Ventilation and Heat Recovery | Ottawa¦Poor ¦ASHP¦Propane ¦Demand Control Ventilation and Heat Recovery | -21.8 | 28.9 | 84 | 45 | -56 | -97.4% | -299 | 3.7 | 3.5 | 301029 | 29.8% | 31772
Thunder Bay | Good | ASHP | Propane | Demand Control Ventilation and Heat Recovery | Thunder Bay¦Good¦ASHP¦Propane ¦Demand Control Ventilation and Heat Recovery | -27 | 27 | 64 | 32.5 | -45.8 | -97.6% | -286 | 3.6 | 3.6 | 239389 | 29.5% | 25411
Thunder Bay | Medium | ASHP | Propane | Demand Control Ventilation and Heat Recovery | Thunder Bay¦Medium¦ASHP¦Propane ¦Demand Control Ventilation and Heat Recovery | -27 | 27 | 77 | 38 | -55.1 | -97.6% | -295 | 3.8 | 3.4 | 293817 | 31.2% | 30544
Thunder Bay | Poor | ASHP | Propane | Demand Control Ventilation and Heat Recovery | Thunder Bay¦Poor ¦ASHP¦Propane ¦Demand Control Ventilation and Heat Recovery | -27 | 27 | 86 | 43.5 | -61.5 | -97.6% | -299 | 3.9 | 3.3 | 331099 | 31.9% | 34142
Toronto | Good | ASHP | Propane | Demand Control Ventilation and Heat Recovery | Toronto¦Good¦ASHP¦Propane ¦Demand Control Ventilation and Heat Recovery | -17.1 | 28.8 | 55 | 34 | -36.8 | -97.3% | -276 | 3.2 | 4.1 | 188440 | 26% | 21069
Toronto | Medium | ASHP | Propane | Demand Control Ventilation and Heat Recovery | Toronto¦Medium¦ASHP¦Propane ¦Demand Control Ventilation and Heat Recovery | -17.1 | 28.8 | 65 | 40 | -43.5 | -97.3% | -286 | 3.4 | 3.9 | 227730 | 27.3% | 24892
Toronto | Poor | ASHP | Propane | Demand Control Ventilation and Heat Recovery | Toronto¦Poor ¦ASHP¦Propane ¦Demand Control Ventilation and Heat Recovery | -17.1 | 28.8 | 75 | 45 | -50.2 | -97.3% | -293 | 3.5 | 3.7 | 266950 | 28.5% | 28675
Kingston | Good | ASHP | Propane | Demand Control Ventilation and Heat Recovery | Kingston¦Good¦ASHP¦Propane ¦Demand Control Ventilation and Heat Recovery | -19 | 26.1 | 58 | 32 | -38 | -97% | -280 | 3.1 | 4.2 | 196324 | 25.1% | 22259
Kingston | Medium | ASHP | Propane | Demand Control Ventilation and Heat Recovery | Kingston¦Medium¦ASHP¦Propane ¦Demand Control Ventilation and Heat Recovery | -19 | 26.1 | 69 | 37 | -45.1 | -97.3% | -292 | 3.4 | 3.8 | 238595 | 28% | 25794
Kingston | Poor | ASHP | Propane | Demand Control Ventilation and Heat Recovery | Kingston¦Poor ¦ASHP¦Propane ¦Demand Control Ventilation and Heat Recovery | -19 | 26.1 | 80 | 43 | -52.2 | -97.3% | -299 | 3.6 | 3.6 | 281017 | 29.1% | 29911
Ottawa | Good | ASHP hybrid system | Natural Gas | Demand Control Ventilation and Heat Recovery | Ottawa¦Good¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -21.8 | 28.9 | 60 | 35 | -31.8 | -94.3% | 77.1 | 1.5 | 8.3 | 33847 | 11.3% | 8441
Ottawa | Medium | ASHP hybrid system | Natural Gas | Demand Control Ventilation and Heat Recovery | Ottawa¦Medium¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -21.8 | 28.9 | 70 | 40 | -37.1 | -94.3% | 66.35 | 1.6 | 7.8 | 44053 | 12.2% | 9814
Ottawa | Poor | ASHP hybrid system | Natural Gas | Demand Control Ventilation and Heat Recovery | Ottawa¦Poor ¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -21.8 | 28.9 | 84 | 45 | -44.4 | -94.3% | 54.84 | 1.7 | 7.2 | 58679 | 13.4% | 11656
Thunder Bay | Good | ASHP hybrid system | Natural Gas | Demand Control Ventilation and Heat Recovery | Thunder Bay¦Good¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -27 | 27 | 64 | 32.5 | -36.3 | -94.7% | 76.75 | 1.6 | 7.8 | 38846 | 12.1% | 8914
Thunder Bay | Medium | ASHP hybrid system | Natural Gas | Demand Control Ventilation and Heat Recovery | Thunder Bay¦Medium¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -27 | 27 | 77 | 38 | -43.7 | -94.7% | 65.06 | 1.7 | 7.2 | 52594 | 13.3% | 10696
Thunder Bay | Poor | ASHP hybrid system | Natural Gas | Demand Control Ventilation and Heat Recovery | Thunder Bay¦Poor ¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -27 | 27 | 86 | 43.5 | -48.8 | -94.7% | 60.05 | 1.7 | 7 | 61561 | 13.8% | 11973
Toronto | Good | ASHP hybrid system | Natural Gas | Demand Control Ventilation and Heat Recovery | Toronto¦Good¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -17.1 | 28.8 | 55 | 34 | -28.3 | -94.3% | 83.54 | 1.4 | 8.6 | 29011 | 10.7% | 7846
Toronto | Medium | ASHP hybrid system | Natural Gas | Demand Control Ventilation and Heat Recovery | Toronto¦Medium¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -17.1 | 28.8 | 65 | 40 | -34.6 | -94.3% | 70.92 | 1.5 | 8 | 39284 | 11.7% | 9265
Toronto | Poor | ASHP hybrid system | Natural Gas | Demand Control Ventilation and Heat Recovery | Toronto¦Poor ¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -17.1 | 28.8 | 75 | 45 | -39.9 | -94.3% | 61.67 | 1.6 | 7.6 | 49553 | 12.6% | 10643
Kingston | Good | ASHP hybrid system | Natural Gas | Demand Control Ventilation and Heat Recovery | Kingston¦Good¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -19 | 26.1 | 58 | 32 | -30.3 | -95% | 77.46 | 1.5 | 8.3 | 32186 | 11.2% | 8111
Kingston | Medium | ASHP hybrid system | Natural Gas | Demand Control Ventilation and Heat Recovery | Kingston¦Medium¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -19 | 26.1 | 69 | 37 | -36 | -94.9% | 64.1 | 1.6 | 7.7 | 43758 | 12.4% | 9603
Kingston | Poor | ASHP hybrid system | Natural Gas | Demand Control Ventilation and Heat Recovery | Kingston¦Poor ¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation and Heat Recovery | -19 | 26.1 | 80 | 43 | -41.8 | -94.9% | 54.7 | 1.7 | 7.3 | 55220 | 13.2% | 11139
Ottawa | Good | ASHP hybrid system | Propane | Demand Control Ventilation and Heat Recovery | Ottawa¦Good¦ASHP hybrid system¦Propane ¦Demand Control Ventilation and Heat Recovery | -21.8 | 28.9 | 60 | 35 | -39.2 | -95.3% | -339 | 4.3 | 3 | 228651 | 34.6% | 23881
Ottawa | Medium | ASHP hybrid system | Propane | Demand Control Ventilation and Heat Recovery | Ottawa¦Medium¦ASHP hybrid system¦Propane ¦Demand Control Ventilation and Heat Recovery | -21.8 | 28.9 | 70 | 40 | -45.7 | -95.3% | -347 | 4.6 | 2.9 | 271325 | 36.8% | 26660
Ottawa | Poor | ASHP hybrid system | Propane | Demand Control Ventilation and Heat Recovery | Ottawa¦Poor ¦ASHP hybrid system¦Propane ¦Demand Control Ventilation and Heat Recovery | -21.8 | 28.9 | 84 | 45 | -54.8 | -95.4% | -357 | 4.9 | 2.6 | 331304 | 39.8% | 31870
Thunder Bay | Good | ASHP hybrid system | Propane | Demand Control Ventilation and Heat Recovery | Thunder Bay¦Good¦ASHP hybrid system¦Propane ¦Demand Control Ventilation and Heat Recovery | -27 | 27 | 64 | 32.5 | -44.9 | -95.6% | -340 | 4.8 | 2.7 | 262508 | 38.6% | 25490
Thunder Bay | Medium | ASHP hybrid system | Propane | Demand Control Ventilation and Heat Recovery | Thunder Bay¦Medium¦ASHP hybrid system¦Propane ¦Demand Control Ventilation and Heat Recovery | -27 | 27 | 77 | 38 | -54 | -95.7% | -349 | 5.2 | 2.5 | 321582 | 41.5% | 30638
Thunder Bay | Poor | ASHP hybrid system | Propane | Demand Control Ventilation and Heat Recovery | Thunder Bay¦Poor ¦ASHP hybrid system¦Propane ¦Demand Control Ventilation and Heat Recovery | -27 | 27 | 86 | 43.5 | -60.3 | -95.7% | -353 | 5.3 | 2.5 | 361956 | 42.7% | 34245
Toronto | Good | ASHP hybrid system | Propane | Demand Control Ventilation and Heat Recovery | Toronto¦Good¦ASHP hybrid system¦Propane ¦Demand Control Ventilation and Heat Recovery | -17.1 | 28.8 | 55 | 34 | -36.1 | -95.3% | -333 | 4.1 | 3.2 | 208270 | 33.1% | 21133
Toronto | Medium | ASHP hybrid system | Propane | Demand Control Ventilation and Heat Recovery | Toronto¦Medium¦ASHP hybrid system¦Propane ¦Demand Control Ventilation and Heat Recovery | -17.1 | 28.8 | 65 | 40 | -42.7 | -95.3% | -343 | 4.4 | 3 | 251136 | 35.3% | 24968
Toronto | Poor | ASHP hybrid system | Propane | Demand Control Ventilation and Heat Recovery | Toronto¦Poor ¦ASHP hybrid system¦Propane ¦Demand Control Ventilation and Heat Recovery | -17.1 | 28.8 | 75 | 45 | -52.6 | -95.6% | -344 | 4.8 | 2.7 | 310377 | 39% | 30052
Kingston | Good | ASHP hybrid system | Propane | Demand Control Ventilation and Heat Recovery | Kingston¦Good¦ASHP hybrid system¦Propane ¦Demand Control Ventilation and Heat Recovery | -19 | 26.1 | 58 | 32 | -37.4 | -96% | -334 | 4.2 | 3.1 | 216256 | 34% | 21767
Kingston | Medium | ASHP hybrid system | Propane | Demand Control Ventilation and Heat Recovery | Kingston¦Medium¦ASHP hybrid system¦Propane ¦Demand Control Ventilation and Heat Recovery | -19 | 26.1 | 69 | 37 | -44.4 | -95.8% | -347 | 4.6 | 2.9 | 263077 | 36.8% | 25853
Kingston | Poor | ASHP hybrid system | Propane | Demand Control Ventilation and Heat Recovery | Kingston¦Poor ¦ASHP hybrid system¦Propane ¦Demand Control Ventilation and Heat Recovery | -19 | 26.1 | 80 | 43 | -51.5 | -95.8% | -354 | 4.8 | 2.7 | 309344 | 38.7% | 29978
Ottawa | Good | ASHP | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Ottawa¦Good¦ASHP¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -21.8 | 28.9 | 60 | 35 | -33.3 | -98.7% | -19.22 | 2 | 6.3 | 72193 | 16.2% | 11441
Ottawa | Medium | ASHP | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Ottawa¦Medium¦ASHP¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -21.8 | 28.9 | 70 | 40 | -38.8 | -98.7% | -28.84 | 2.1 | 5.9 | 88489 | 17.2% | 13311
Ottawa | Poor | ASHP | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Ottawa¦Poor ¦ASHP¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -21.8 | 28.9 | 84 | 45 | -46.5 | -98.8% | -45.66 | 2.4 | 5.3 | 115097 | 19.4% | 15842
Thunder Bay | Good | ASHP | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Thunder Bay¦Good¦ASHP¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -27 | 27 | 64 | 32.5 | -37.8 | -99.3% | -25.22 | 2.4 | 5.1 | 84719 | 20% | 11553
Thunder Bay | Medium | ASHP | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Thunder Bay¦Medium¦ASHP¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -27 | 27 | 77 | 38 | -45.7 | -99% | -31.65 | 2.3 | 5.4 | 105723 | 19.2% | 14762
Thunder Bay | Poor | ASHP | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Thunder Bay¦Poor ¦ASHP¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -27 | 27 | 86 | 43.5 | -51.1 | -99% | -40.34 | 2.5 | 5.1 | 123189 | 20.3% | 16518
Toronto | Good | ASHP | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Toronto¦Good¦ASHP¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -17.1 | 28.8 | 55 | 34 | -30.6 | -98.7% | -2.11 | 1.8 | 6.9 | 60464 | 14.5% | 10613
Toronto | Medium | ASHP | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Toronto¦Medium¦ASHP¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -17.1 | 28.8 | 65 | 40 | -36.2 | -98.7% | -21.89 | 2 | 6.2 | 79666 | 16.3% | 12535
Toronto | Poor | ASHP | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Toronto¦Poor ¦ASHP¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -17.1 | 28.8 | 75 | 45 | -41.8 | -98.7% | -36.33 | 2.2 | 5.7 | 98810 | 17.9% | 14412
Kingston | Good | ASHP | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Kingston¦Good¦ASHP¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -19 | 26.1 | 58 | 32 | -31.6 | -98.4% | -15.37 | 1.9 | 6.8 | 67249 | 14.7% | 11561
Kingston | Medium | ASHP | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Kingston¦Medium¦ASHP¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -19 | 26.1 | 69 | 37 | -37.5 | -98.7% | -31.78 | 2.1 | 5.9 | 86703 | 17.2% | 13010
Kingston | Poor | ASHP | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Kingston¦Poor ¦ASHP¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -19 | 26.1 | 80 | 43 | -43.4 | -98.7% | -46.26 | 2.3 | 5.5 | 107744 | 18.9% | 15089
Ottawa | Good | ASHP | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Ottawa¦Good¦ASHP¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -21.8 | 28.9 | 60 | 35 | -40.7 | 99% | -396 | 4.5 | 2.9 | 264242 | 36.6% | 25880
Ottawa | Medium | ASHP | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Ottawa¦Medium¦ASHP¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -21.8 | 28.9 | 70 | 40 | -47.5 | -99% | -431 | 5.8 | 2.2 | 327088 | 46.6% | 30157
Ottawa | Poor | ASHP | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Ottawa¦Poor ¦ASHP¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -21.8 | 28.9 | 84 | 45 | -56.9 | -99% | -424 | 5.6 | 2.3 | 387823 | 44.9% | 36057
Thunder Bay | Good | ASHP | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Thunder Bay¦Good¦ASHP¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -27 | 27 | 64 | 32.5 | -45.6 | -99.2% | -399 | 5.1 | 2.6 | 303704 | 41.1% | 28872
Thunder Bay | Medium | ASHP | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Thunder Bay¦Medium¦ASHP¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -27 | 27 | 77 | 38 | -56 | -99.2% | -414 | 5.7 | 2.3 | 374788 | 46% | 34705
Thunder Bay | Poor | ASHP | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Thunder Bay¦Poor ¦ASHP¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -27 | 27 | 86 | 43.5 | -62.5 | -99.2% | -421 | 6.1 | 2.2 | 423649 | 48.5% | 38792
Toronto | Good | ASHP | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Toronto¦Good¦ASHP¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -17.1 | 28.8 | 55 | 34 | -37.5 | -98.9% | -388 | 4.3 | 3.1 | 239760 | 34.5% | 23900
Toronto | Medium | ASHP | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Toronto¦Medium¦ASHP¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -17.1 | 28.8 | 65 | 40 | -44.3 | -98.9% | -404 | 4.7 | 2.8 | 291517 | 38% | 28238
Toronto | Poor | ASHP | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Toronto¦Poor ¦ASHP¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -17.1 | 28.8 | 75 | 45 | -54.6 | -99.2% | -409 | 5.4 | 2.4 | 362465 | 43.2% | 34031
Kingston | Good | ASHP | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Kingston¦Good¦ASHP¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -19 | 26.1 | 58 | 32 | -38.7 | -98.7% | -397 | 4.2 | 3.1 | 251496 | 33.7% | 25219
Kingston | Medium | ASHP | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Kingston¦Medium¦ASHP¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -19 | 26.1 | 69 | 37 | -45.8 | -98.8% | -412 | 5 | 2.6 | 305920 | 39.9% | 29259
Kingston | Poor | ASHP | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Kingston¦Poor ¦ASHP¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -19 | 26.1 | 80 | 43 | -53.1 | -98.9% | -424 | 5.4 | 2.4 | 361909 | 43.2% | 33929
Ottawa | Good | ASHP hybrid system | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Ottawa¦Good¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -21.8 | 28.9 | 60 | 35 | -33.1 | -98.1% | -26.87 | 2.1 | 6.1 | 74661 | 16.8% | 11458
Ottawa | Medium | ASHP hybrid system | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Ottawa¦Medium¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -21.8 | 28.9 | 70 | 40 | -38.6 | -98.2% | -44.58 | 2.3 | 5.5 | 94924 | 18.8% | 13331
Ottawa | Poor | ASHP hybrid system | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Ottawa¦Poor ¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -21.8 | 28.9 | 84 | 45 | -46.3 | -98.2% | -60.75 | 2.6 | 4.9 | 122411 | 21.3% | 15866
Thunder Bay | Good | ASHP hybrid system | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Thunder Bay¦Good¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -27 | 27 | 64 | 32.5 | -37.8 | -98.5% | -32.24 | 2.3 | 5.4 | 87639 | 19% | 12315
Thunder Bay | Medium | ASHP hybrid system | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Thunder Bay¦Medium¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -27 | 27 | 77 | 38 | -45.4 | -98.5% | -45.69 | 2.5 | 4.9 | 112431 | 21% | 14785
Thunder Bay | Poor | ASHP hybrid system | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Thunder Bay¦Poor ¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -27 | 27 | 86 | 43.5 | -50.8 | -98.5% | -54.3 | 2.7 | 4.6 | 130614 | 22.3% | 16543
Toronto | Good | ASHP hybrid system | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Toronto¦Good¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -17.1 | 28.8 | 55 | 34 | -30.4 | -98.1% | -22.56 | 2 | 6.3 | 67247 | 16.2% | 10629
Toronto | Medium | ASHP hybrid system | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Toronto¦Medium¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -17.1 | 28.8 | 65 | 40 | -36 | -98.1% | -36.74 | 2.2 | 5.8 | 85321 | 17.6% | 12553
Toronto | Poor | ASHP hybrid system | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Toronto¦Poor ¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -17.1 | 28.8 | 75 | 45 | -41.5 | -98.1% | -51.26 | 2.4 | 5.3 | 105336 | 19.4% | 14434
Kingston | Good | ASHP hybrid system | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Kingston¦Good¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -19 | 26.1 | 58 | 32 | -31.4 | -98.3% | -26.46 | 2 | 6.2 | 70690 | 16.5% | 10992
Kingston | Medium | ASHP hybrid system | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Kingston¦Medium¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -19 | 26.1 | 69 | 37 | -37.3 | -98.3% | -46.18 | 2.3 | 5.5 | 92509 | 18.7% | 13023
Kingston | Poor | ASHP hybrid system | Natural Gas | Demand Control Ventilation, Air Sealing and Heat Recovery | Kingston¦Poor ¦ASHP hybrid system¦Natural Gas¦Demand Control Ventilation, Air Sealing and Heat Recovery | -19 | 26.1 | 80 | 43 | -43.2 | -98.2% | -61.04 | 2.5 | 5 | 114594 | 20.6% | 15106
Ottawa | Good | ASHP hybrid system | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Ottawa¦Good¦ASHP hybrid system¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -21.8 | 28.9 | 60 | 35 | -40.5 | -98.5% | -410 | 4.9 | 2.7 | 269466 | 39.1% | 25897
Ottawa | Medium | ASHP hybrid system | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Ottawa¦Medium¦ASHP hybrid system¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -21.8 | 28.9 | 70 | 40 | -47.3 | -98.5% | -424 | 5.4 | 2.4 | 321755 | 43.2% | 30176
Ottawa | Poor | ASHP hybrid system | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Ottawa¦Poor ¦ASHP hybrid system¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -21.8 | 28.9 | 84 | 45 | -56.7 | -98.5% | -438 | 6.1 | 2.1 | 395137 | 48.8% | 36081
Thunder Bay | Good | ASHP hybrid system | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Thunder Bay¦Good¦ASHP hybrid system¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -27 | 27 | 64 | 32.5 | -46.3 | -98.8% | -412 | 5.5 | 2.4 | 309186 | 44.1% | 28890
Thunder Bay | Medium | ASHP hybrid system | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Thunder Bay¦Medium¦ASHP hybrid system¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -27 | 27 | 77 | 38 | 55.7 | -98.7% | -427 | 6.2 | 2.1 | 381496 | 49.9% | 34728
Thunder Bay | Poor | ASHP hybrid system | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Thunder Bay¦Poor ¦ASHP hybrid system¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -27 | 27 | 86 | 43.5 | -62.2 | -98.8% | -434 | 6.6 | 2 | 431065 | 52.8% | 38816
Toronto | Good |  |  | Demand Control Ventilation, Air Sealing and Heat Recovery | Toronto¦Good¦¦¦Demand Control Ventilation, Air Sealing and Heat Recovery | -17.1 | 28.8 | 55 | 34 | -37.3 | -98.5% | -402 | 4.6 | 2.9 | 244508 | 36.7% | 23916
Toronto | Medium |  |  | Demand Control Ventilation, Air Sealing and Heat Recovery | Toronto¦Medium¦¦¦Demand Control Ventilation, Air Sealing and Heat Recovery | -17.1 | 28.8 | 65 | 40 | -44.1 | -98.5% | -418 | 5.1 | 2.6 | 297172 | 40.8% | 28256
Toronto | Poor |  |  | Demand Control Ventilation, Air Sealing and Heat Recovery | Toronto¦Poor ¦¦¦Demand Control Ventilation, Air Sealing and Heat Recovery | -17.1 | 28.8 | 75 | 45 | -50.8 | -98.5% | -430 | 5.6 | 2.4 | 39780 | 44.6% | 32552
Kingston | Good | ASHP hybrid system | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Kingston¦Good¦ASHP hybrid system¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -19 | 26.1 | 58 | 32 | -38.4 | -98.6% | -409 | 4.8 | 2.8 | 254979 | 38.3% | 24651
Kingston | Medium | ASHP hybrid system | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Kingston¦Medium¦ASHP hybrid system¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -19 | 26.1 | 69 | 37 | -45.7 | -98.6% | -425 | 5.4 | 2.4 | 311818 | 42.9% | 29273
Kingston | Poor | ASHP hybrid system | Propane | Demand Control Ventilation, Air Sealing and Heat Recovery | Kingston¦Poor ¦ASHP hybrid system¦Propane ¦Demand Control Ventilation, Air Sealing and Heat Recovery | -19 | 26.1 | 80 | 43 | -53 | -98.6% | -437 | 5.8 | 2.2 | 368556 | 46.8% | 32132
Note on P128: Mintou Ndiaye: Grosse hausse pour les systemes hybrides