## M&V Plan
1. Project Description and Methodology
Project description | What is the project?
In describing the project, it can be helpful to include the existing conditions as a reference, what is being installed or changed, the quantities involved, and any additions or controls included in the project. You can use a table such as the one below, create multiple tables if needed, or import a description from another file. Often existing and baseline are the same. In some cases, the baseline equipment and/or operating conditions could be different than existing. Existing and baseline may differ when existing equipment is not meeting current service needs, or the service needs are changing (e.g. facility change of use or occupancy schedules). Example: Baseline is a larger screw chiller (replace-in-kind, but larger), but the project is to invest in a more expensive and efficient chiller.
| Baseline Equipment and Operating Conditions | Project Equipment and Operating Conditions
Equipment type | Screw chiller | VFD chiller
Equipment unitary wattage (kW, HP, tons) | 150 tons | 125 tons
Equipment quantity | 1 | 1
Operating hours | 1600 | 1500
Controls | None | VFD
Other
Measurement Boundary | What is measured and where? For how long?
It can be helpful to show schematically what will be measured. If using a sampling approach, this should be documented. To determine the measurement approach, consider whether the load is consistent, or if it is expected to vary based on an external factor (temperature, occupancy, etc.) State whether interactive effects may apply, and if the M&V will quantify interactions. (E.g. upgrade to more efficient refrigeration equipment may increase load on space heating system in winter, and decrease load on space cooling in summer.)
Sampling approach used? | Yes/No; if yes, specify how many measurements will be taken. To decide on sampling, consider whether you have: (1) a large quantity of equipment in your project, or (2) if the equipment operates on a wide range of parameters (e.g. temperature).
Impact on other fuels? | If the project's objective is to save electricity, will the project substantially impact (increase or decrease) other energy forms purchased by the facility such as natural gas or biofuels? If so, the M&V Plan should address how these impacts will be measured or estimated.
Measured Values | Baseline Conditions | Project
Wattage (energy consumption) | Measured; for one week | Measured; for one week
Temperature (variable) | Measured concurrent to above | Measured concurrent to above
Note: More than one parameter can be measured (wattage and operating hours). This is just an example. Refer to specific program requirements if you are applying for incentive.
Estimated or Stipulated Values | What are the assumptions (values that are used but not measured)?
This will allow a third party to follow your thought process.
It is assumed that the energy use varies with temperature. Therefore, equipment load (e.g. chiller tons, air flow, etc.) is not measured.
2. Energy and Demand Savings Calculations
Baseline Period Energy | How is the baseline energy calculated? How will it be adjusted?
Basic equations: | Baseline Period Energy = Sum of (Baseline kW x Baseline Operating Hours) in each baseline temperature bin
Adjusted Baseline Period Energy = Sum of (Baseline kW x Reporting Operating Hours) in each Reporting temperature bin
You can add project specific values, assumptions and justifications here. In cases where the baseline scenario is hypothetical or when baseline data are missing, then baseline energy may be calculated using engineering equations or simulated using commercial software.
Reporting Period Energy | How is the reporting energy calculated?
Basic equation: | Reporting Period Energy = Sum of (Reporting kW x Reporting Operating Hours) in each Reporting temperature bin
You can add project-specific values, assumptions and justifications here.
Savings Calculation | How are the savings calculated?
Basic equation: | Energy Savings = Adjusted Baseline Period Energy - Reporting Period Energy
You can add project-specific values, assumptions and justifications here.
Anticipated Energy Savings | What are the anticipated energy savings?
This is calculated based on the above equations. You can enter the savings value here so it can be compared to the actual results in the M&V Report.
Energy Savings =
Impact on Other Fuels | If expected, what are the impacts on other fuels?
State how impacts on other fuels (e.g. natural gas, biomass, propane, diesel fuel) will be measured or estimated.
Other fuels impact =
3. Optional Reporting
If required by your organization, you can track additional metrics in this section.
Cost savings | Utility bill cost savings; specify marginal utility rates for energy and (if applicable) demand savings Maintenance cost savings (or increased maintenance, if applicable)
Utility Cost Savings = kWh rate x kWh annual savings + kW rate x kW savings
Maintenance Cost Savings =
Annual Cost Savings = Utility Cost Savings + Maintenance Cost Savings
GHG emissions reduction
| Electricity factor (kg CO2 eq/kWh) | 0.03
| Natural gas factor (kg CO2 eq/m3) | 1.921
GHG emissions reductions = GHG Factor x Energy Savings
Simple project payback | Simple project payback (years) = Total Project Cost / Annual Cost Savings
4. Operational Verification
Once the project has been implemented, conducting an operational verification will help you prepare for savings reporting.
Complete the site verification form | Link

## M&V Report Template
1. Project Description and Methodology
Project description | What is the project?
Copy from M&V Plan, make sure to mention anything that has changed since M&V Plan was developed. In describing the project, it can be helpful to include the existing conditions as a reference, what is being installed or changed, the quantities involved, and any additions or controls included in the project. You can use a table such as the one below, create multiple tables if needed or import a description from another file. Often existing and baseline are the same. In some cases, the baseline equipment and/or operating conditions could be different than existing. Existing and baseline may differ when existing equipment is not meeting current service needs, or the service needs are changing (e.g. facility change of use or occupancy schedules). Example: Baseline is a larger screw chiller (replace-in-kind, but larger), but the project is to invest in a more expensive and efficient chiller.
| Baseline Equipment and Operating Conditions | Installed Project Equipment and Operating Conditions
Copy from M&V Plan, make sure to mention anything that has changed since M&V Plan was developed.
Equipment type | Screw chiller | VFD chiller
Equipment unitary wattage (kW, HP, tons) | 150 tons | 125 tons
Equipment quantity | 1 | 1
Operating hours | 1600 | 1500
Controls | None | VFD
Other
Measurement Boundary | What is measured and where? For how long?
Copy from M&V Plan, make sure to mention anything that has changed since M&V Plan was developed. It can be helpful to show schematically what will be measured. If using a sampling approach, this should be documented. To determine the measurement approach, consider whether the load is consistent, or if it is expected to vary based on an external factor (temperature, occupancy, etc.). State whether interactive effects may apply, and if the M&V will quantify interactions. (E.g. upgrade to more efficient refrigeration equipment may increase load on space heating system in winter, and decrease load on space cooling in summer.)
Sampling approach used? | Yes/No; if yes, specify how many measurements will be taken. To decide on sampling, consider whether you have: (1) a large quantity of equipment in your project, or (2) if the equipment operates on a wide range of parameters (e.g. temperature).
Impact on other fuels? | If the project's objective is to save electricity, will the project substantially impact (increase or decrease) other energy forms purchased by the facility, such as natural gas or biofuels? If so, the M&V Plan should address how these impacts will be measured or estimated.
Measured Values | Baseline Conditions | Project
Enter real metering conditions (start and end date, measurement intervals, link to raw data measured/add raw data tabs to this file).
Wattage (energy consumption) | Measured; for one week | Measured; for one week
Temperature (variable) | Measured concurrent to above | Measured concurrent to above
Note: More than one parameter can be measured (wattage and operating hours). This is just an example. Refer to specific program requirements if you are applying for incentive.
Estimated or Stipulated Values | What are the assumptions (values that are used but not measured)?
Copy from the M&V Plan. This will allow a third party to follow your thought process.
It is assumed that the energy use varies with temperature. Therefore, equipment load (e.g., chiller tons, air flow, etc.) is not measured.
2. Energy and Demand Savings Calculations
Baseline Period Energy | How is the baseline energy calculated? How will it be adjusted?
Basic equations: | Baseline Period Energy = Sum of (Baseline kW x Baseline Operating Hours) in each baseline temperature bin
Adjusted Baseline Period Energy = Sum of (Baseline kW x Reporting Operating Hours) in each Reporting temperature bin
Update the equations if they have changed since the M&V Plan was developed. Enter actual numbers, which can be calculated in the separate tabs if you are using raw data. You can add project-specific values, assumptions and justifications here. In cases where the baseline scenario is hypothetical or when baseline data are missing, then baseline energy may be calculated using engineering equations or simulated using commercial software.
Reporting Period Energy | How is the reporting energy calculated?
Basic equation: | Reporting Period Energy = Sum of (Reporting kW x Reporting Operating Hours) in each Reporting temperature bin
Update the equations as needed. Enter actual numbers, which can be calculated in the separate tabs if you are using raw data.
Savings Calculation | How are the savings calculated?
Basic equation: | Energy Savings = Adjusted Baseline Period Energy - Reporting Period Energy
Update the equations as needed. Enter actual numbers, which can be calculated in the separate tabs if you are using raw data.
Anticipated Energy Savings | What are the anticipated energy savings?
This is calculated based on the above equations. You can compare this value to the anticipated savings you had in the M&V Plan.
Energy Savings =
Impact on Other Fuels | If expected, what are the impacts on other fuels?
Enter actual calculated numbers.
Other fuels impact =
3. Optional Reporting
If required by your organization, you can track additional metrics in this section.
Cost savings | Enter actual numbers, based on above calculations. Utility bill cost savings; specify marginal utility rates for energy and (if applicable) demand savings. Maintenance cost savings (or increased maintenance, if applicable).
Utility Cost Savings = kWh rate x kWh annual savings + kW rate x kW savings
Maintenance Cost Savings =
Annual Cost Savings = Utility Cost Savings + Maintenance Cost Savings
GHG emissions reduction
| Electricity factor (kg CO2 eq/kWh) | 0.03
| Natural gas factor (kg CO2 eq/m3) | 1.921
GHG emissions reductions = GHG Factor x Energy Savings
Simple project payback | Simple project payback (years) = Total Project Cost / Annual Cost Savings
4. Operational Verification
Update the site verification form and link it here
Complete the site verification form | Link
Note on E1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Context, change «PLAN» to «REPORT» Change colors so it’s clear this is a different step (maybe IESO blue or orange?)
Note on A30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Suggest deleting this since it’s repeated from the cell above.