## M&V Plan
1. Project Description and Methodology
Project description | What is the project?
In describing the project, it can be helpful to include the existing conditions as a reference, what is being installed or changed, the quantities involved, and any additions or controls included in the project. You can use a table such as the one below, create multiple tables if needed or import a description from another file.
| Baseline Building and Operating Conditions | Proposed Building and Operating Conditions
Equipment type | Existing building conditions | Existing building commissioning project
Equipment unitary wattage (kW, HP, tons) | N/A - entire building | N/A - entire building
Equipment quantity | N/A - entire building | N/A - entire building
Operating hours | 8760 | 8760
Controls | Existing controls, inefficient situation | Optimized runtime, schedule, setpoints
Other
Measurement Boundary | What is measured and where? For how long?
It can be helpful to show schematically what will be measured. In the case of Option C, this includes the main meter for energy consumption, but also the variables used for adjusting the baseline.
Impact on other fuels? | If the project's objective is to save electrcity, will the project substantially impact (increase or decrease) other energy forms purchased by the facility such as natural gas or biofuels? If so, the M&V Plan should address how these impacts will be measured or estimated.
Measured Values | Baseline Conditions | Project
kWh (energy consumption) | Measured over three months to cover full range | Measured over three months to cover full range
Temperature (variable) | From weather station, concurrent to above | From weather station, concurrent to above
Estimated or Stipulated Values | What are the assumptions (values that are used but not measured)?
This will allow a third party to follow your thought process.
It is assumed that the energy use varies with temperature. The effects of occupancy are deemed to be negligible.
Anticipated Routine Adjustments | How will consumption be adjusted for reporting period conditions? What are the variables used?
It is assumed that the energy use varies with temperature. Temperature data will be collected for a year following implementation of the project. Savings will be extrapolated to a full year using annual weather data.
Non-Routine Adjustments (Static Factors) | How will consumption be adjusted for reporting period conditions? What are the variables used?
List all factors that are deemed static, and explain how they will be tracked. Explain how adjustments will be made if these factors change in the reporting period.
Static Factor | Tracking | Basis for adjustment
Occupancy | Currently 70%; tracked through lease of space | If changed by 10% or more, adjustment will be calculated using typical loads (W/m2).
Equipment replacement | Maintenance logs | If heating or cooling system elements are replaced, adjustments will be made based on the efficiency gains.
Significant retrofits | Capital plan | If significant projects (envelope retrofit, equipment improvement, etc.) are made that are not part of this project, the impact of these changes will be deducted from the energy savings calculated through this model.
2. Energy and Demand Savings Calculations
Baseline Period Energy | How is the baseline energy calculated? How will it be adjusted?
Basic equations: | Baseline daily kW = a x (Baseline daily Temp) + b
Baseline Period Energy = Sum of (Baseline daily kW) over 365 days
Note: a and b are the baseline model coefficients, where "a" represents the slope and 'b" represents the intercept.
You can add project-specific values, assumptions and justifications here. Note that the equation may look different if you are using multiple variables, e.g.: Baseline daily kW = a x (Baseline daily Temp) + b x (Production Volume) + c
Adjusted Baseline Period Energy | How is the adjusted baseline energy calculated?
Basic equation: | Adjusted Baseline daily kW = a x (Reporting daily Temp) + b
Adjusted Baseline Period Energy = Sum of (Adjusted Baseline daily kW) over 365 days
You can add project-specific values, assumptions and justifications here. Note that the equation may look different if you are using multiple variables, e.g.: Baseline daily kW = a x (Baseline daily Temp) + b x (Production Volume) + c
Reporting Period Energy | How is the reporting energy calculated?
Basic equation: | Reporting daily kW = a x (Reporting daily Temp) + b
Reporting Period Energy = Sum of (Reporting daily kW) over 365 days
You can add project-specific values, assumptions and justifications here. Note that the equation may look different if you are using multiple variables, e.g.: Baseline daily kW = a x (Baseline daily Temp) + b x (Production Volume) + c When extrapolating, you typically need to create a regression for both the baseline and the reporting period.
Savings Calculation | How are the savings calculated?
Basic equation: | Energy Savings = Adjusted Baseline Period Energy - Reporting Period Energy
You can add project-specific values, assumptions and justifications here.
Anticipated Energy Savings | What are the anticipated energy savings?
This is calculated based on the above equations. You can enter the savings value here so it can be compared to the actual results in the M&V Report.
Energy Savings =
Impact on Other Fuels | If expected, what are the impacts on other fuels?
State how impacts on other fuels (e.g. natural gas, biomass, propane, diesel fuel) will be measured or estimated.
Other fuels impact =
3. Optional Reporting
If required by your organization, you can track additional metrics in this section.
Cost analysis | Utility bill cost savings; specify marginal utility rates for energy and (if applicable) demand savings Maintenance cost savings (or increased maintenance, if applicable)
Utility Cost Savings = kWh rate x kWh annual savings + kW rate x kW savings
Maintenance Cost Savings =
Annual Cost Savings = Utility Cost Savings + Maintenance Cost Savings
GHG emissions reduction
| Electricity factor (kg CO2 eq/kWh) | 0.03
| Natural gas factor (kg CO2 eq/m3) | 1.921
GHG emissions reductions = GHG Factor x Energy Savings
Simple project payback | Simple project payback (years) = Total Project Cost / Annual Cost Savings
4. Operational Verification
Once the project has been implemented, conducting an operational verification will help you prepare for savings reporting.
Complete the site verification form | Link

## M&V Report Template
1. Project Description and Methodology
Project description | What is the project?
Copy from M&V Plan, make sure to mention anything that has changed since M&V Plan was developed. In describing the project, it can be helpful to include the existing conditions as a reference, what is being installed or changed, the quantities involved, and any additions or controls included in the project. You can use a table such as the one below, create multiple tables if needed, or import a description from another file.
| Baseline Building and Operating Conditions | Actual Building and Operating Conditions
Copy from M&V Plan, make sure to mention anything that has changed since M&V Plan was developed.
Equipment type | Existing building conditions | Existing building commissioning project
Equipment unitary wattage (kW, HP, tons) | N/A - entire building | N/A - entire building
Equipment quantity | N/A - entire building | N/A - entire building
Operating hours | 8760 | 8760
Controls | Existing controls, inefficient situation | Optimized runtime, schedule, setpoints
Other
Measurement Boundary | What is measured and where? For how long?
Copy from M&V Plan, make sure to mention anything that has changed since M&V Plan was developed. It can be helpful to show schematically what will be measured. In the case of Option C, this includes the main meter for energy consumption, but also the variables used for adjusting the baseline.
Impact on other fuels? | If the project's objective is to save electrcity, will the project substantially impact (increase or decrease) other energy forms purchased by the facility such as natural gas or biofuels? If so, the M&V Plan should address how these impacts will be measured or estimated.
Measured Values | Baseline Conditions | Project
Enter real metering conditions (start and end date, measurement intervals, link to raw data measured/add raw data tabs to this file).
kWh (energy consumption) | Measured over three months to cover full range | Measured over three months to cover full range
Temperature (variable) | From weather station, concurrent to above | From weather station, concurrent to above
Estimated or Stipulated Values | What are the assumptions (values that are used but not measured)?
Copy from the M&V Plan. This will allow a third party to follow your thought process.
It is assumed that the energy use varies with temperature. The effects of occupancy are deemed to be negligible.
Anticipated Routine Adjustments | How will consumption be adjusted for reporting period conditions? What are the variables used?
Update routine adjustment process according to your analysis. It is assumed that the energy use varies with temperature. Temperature data will be collected for a year following implementation of the project. Savings will be extrapolated to a full year using annual weather data.
Non-Routine Adjustments (Static Factors) | How will consumption be adjusted for reporting period conditions? What are the variables used?
Update the static factors to confirm if any have changed during the reporting period. If so, explain non-routine adjustments. List all factors that are deemed static, and explain how they will be tracked. Explain how adjustments will be made if these factors change in the reporting period.
Static Factor | Tracking | Basis for adjustment
Occupancy | Currently 70%; tracked through lease of space | If changed by 10% or more, adjustment will be calculated using typical loads (W/m2).
Equipment replacement | Maintenance logs | If heating or cooling system elements are replaced, adjustments will be made based on the efficiency gains.
Significant retrofits | Capital plan | If significant projects (envelope retrofit, equipment improvement, etc.) are made that are not part of this project, the impact of these changes will be deducted from the energy savings calculated through this model.
2. Energy and Demand Savings Calculations
Baseline Period Energy | How is the baseline energy calculated? How will it be adjusted?
Basic equations: | Baseline daily kW = a x (Baseline daily Temp) + b
Baseline Period Energy = Sum of (Baseline daily kW) over 365 days
Note: a and b are the baseline model coefficients, where "a" represents the slope and 'b" represents the intercept.
You can add project-specific values, assumptions and justifications here. Note that the equation may look different if you are using multiple variables, e.g.: Baseline daily kW = a x (Baseline daily Temp) + b x (Production Volume) + c
Adjusted Baseline Period Energy | How is the adjusted baseline energy calculated?
Basic equation: | Adjusted Baseline daily kW = a x (Reporting daily Temp) + b
Adjusted Baseline Period Energy = Sum of (Adjusted Baseline daily kW) over 365 days
Enter the results of calculations. You can add project-specific values, assumptions and justifications here. Note that the equation may look different if you are using multiple variables, e.g.: Baseline daily kW = a x (Baseline daily Temp) + b x (Production Volume) + c
Reporting Period Energy | How is the reporting energy calculated?
Basic equation: | Reporting daily kW = a x (Reporting daily Temp) + b
Reporting Period Energy = Sum of (Reporting daily kW) over 365 days
Update the equation's factors and enter calculated values. You can add project-specific values, assumptions and justifications here. Note that the equation may look different if you are using multiple variables, e.g.: Baseline daily kW = a x (Baseline daily Temp) + b x (Production Volume) + c When extrapolating, you typically need to create a regression for both the baseline and the reporting period.
Savings Calculation | How are the savings calculated?
Basic equation: | Energy Savings = Adjusted Baseline Period Energy - Reporting Period Energy
Update the equations as needed. Enter actual numbers, which can be calculated in the separate tabs if you are using raw data.
Anticipated Energy Savings | What are the anticipated energy savings?
This is calculated based on the above equations. You can compare this value to the anticipated savings you had in the M&V Plan.
Energy Savings =
Impact on Other Fuels | If expected, what are the impacts on other fuels?
Enter actual calculated numbers.
Other fuels impact =
3. Optional Reporting
If required by your organisation, you can track additional metrics in this section.
Cost analysis | Enter actual numbers, based on above calculations. Utility bill cost savings; specify marginal utility rates for energy and (if applicable) demand savings Maintenance cost savings (or increased maintenance, if applicable)
Utility Cost Savings = kWh rate x kWh annual savings + kW rate x kW savings
Maintenance Cost Savings =
Annual Cost Savings = Utility Cost Savings + Maintenance Cost Savings
GHG emissions reduction
| Electricity factor (kg CO2 eq/kWh) | 0.03
| Natural gas factor (kg CO2 eq/m3) | 1.921
GHG emissions reductions = GHG Factor x Energy Savings
Simple project payback | Simple project payback (years) = Total Project Cost / Annual Cost Savings
4. Operational Verification
Update the site verification form and link it here
Complete the site verification form | Link